# Charlotte Water Scores with GIS:

## Assessing Infiltration and Exfiltration of Groundwater in a Sanitary Sewage Collection System

### By Meredith Moore, Charlotte Water Business Analyst

I recently completed a nine-month research and analysis project for Charlotte Water. Charlotte Water’s sanitary sewer pipe network needed a simple scoring system – one incorporating groundwater elevation, sewer pipe elevation, pipe material, and volume of sewage carried by those pipes. A score would quantify the risk of sewage getting out of the pipe or of groundwater getting into it.

We knew we needed this scoring system thanks to groundwater sampling from 2000. The sampling found high concentrations of fecal coliform bacteria in groundwater, specifically those where sewer pipes sat above the water table. Damaged pipes were letting sewage leak into the surrounding soils and groundwater. Some bacteria reached our streams, potentially harming water resources.

We noticed lower bacterial concentrations where sewer lines sat under the water table. Here, pressure kept sewage from leaking out of the pipe. However, groundwater could infiltrate damaged pipes, so as a result, Charlotte Water was sometimes using its treatment capacities to treat groundwater unnecessarily.

Of course, not all sewer lines above the water table leaked sewage into surrounding soil. Not all sewer lines below the water table were being infiltrated by clean groundwater. Charlotte Water needed a way to determine which pipes were at greatest risk for this exfiltration and infiltration. We needed to quantify this risk.

## A Sound Groundwater Scoring System

Charlotte Water had a wealth of GIS data. This included sewer pipe elevation, which we could compare to groundwater elevation (i.e., the water table). To do this required me to build a GIS layer for groundwater elevation. I created this layer by using regression analysis – on slope, elevation, and known groundwater elevation values. To test my layer’s accuracy, I cross-referenced my layer with already documented infiltration locations from initial CCTV investigations. The layer was accurate!

Now I could compare the water table elevation to our sewer pipes’ elevation. I divided the pipe into two datasets: those above and below the water table. Then I assigned each pipe a score, according to its material and the volume of sewage it carried.

For material type, a score of five indicated a highest-risk pipe (material type: terra cotta) and a score of one indicated the lowest risk pipe (material type: PVC).

For volume, I used consumption data collected from November 2014, which tracked individual meters through sewer pipes and down to wastewater treatment plants. November represented a representative month of consumption, excluding the high-watering months of summer; we also discarded large water consumers, such as the local soda bottling facility. (While customer consumption data does not necessarily equal sewage volume in a collection system, it was a good approximation for our needs!) A score of five indicated the highest volume-carrying pipes, and a score of one indicated the lowest-volume-carrying pipes.

Finally, I summarized the pipes’ material and volume scores. My two output datasets for pipes above and below the water table showed us the potential risk of each pipe for exfiltration and infiltration. The local stormwater utility, CMSWS, can use the scores for sewer pipes above the groundwater elevation to target water-quality monitoring efforts in high-exfiltration risk areas. The utility can use the scores for pipes under the water table to evaluate inflow and infiltration in the Charlotte Water’s collection system.

Both datasets have the potential to help prioritize sewer-line rehabilitation and repair plans.

“By scoring our pipes, we can be more strategic about field service activities,” Charlotte Water Continuous Improvement Officer Regina Dobson Cousar said. “Being strategic about reactive repairs, and hopefully in the future much more predictive about preventive repair, will assist us with our goal to be efficient and effective stewards of community resources.”

#### About the Author and this Project:

This project was Meredith Moore’s capstone project to fulfill the completion of a Master of Geographic Information Systems (MGIS) from Penn State University. Ms. Moore was chosen as Penn State’s Esri Development Center Outstanding Student of the Year (2015) for her performance in this program. To view her presentation, please click here in the online version of this newsletter.

If you have questions about this article, please contact Ms. Moore at msmoore@charlottenc.gov.

“This tool, and other tools like it, are a part of the customer service kit we know we will have to continue to replenish as we move towards heightened operational resiliency.” – Charlotte Water Continuous Improvement Officer Regina Dobson Cousar